## Sheet1
Type Test Report
Motor tested in accordance with IEC60034-2-1 & AS/NZS1359.102.3.Efficiency as per IEC60034-2-1
(PLL determined from residual loss)
SHANGHAI TOP MOTOR CO., LTD
No.303 Kangliu Road |  |  |  | Ph: 86 15000088129 |  |  | Type: | TCI 160L-4
Kang Qiao Industrial Area |  |  |  | zk@techtop.net.cn |  |  | TR Number: | 2012060701
Pudong, Shanghai, China |  |  |  | www.techtop.com |  |  | Test Lab: | Techtop factory
Nameplate:
Type: | TCI 160L-4 |  | Duty: | S1 | IP: | 55
Serial No: | 2012030705 |  | Ins.Cl: | F | KG: | 140
Voltage | Hz | kW | A | cos fi | r/min | Eff.[%]
400/690 | 50 | 15 | 27.4/15.9 | 0.87 | 1470 | 90.9
Brg.DE: | 6309C3 |  | Brg.NDE: | 6309C3
No Load Test:
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
No load | 380 | 8.7467 | 453.5 | 50 | 1500 | 0 | 0 | 0.078775 | 0
No load | 400 | 10.245 | 531 | 50 | 1500 | 0 | 0 | 0.07481 | 0
No load | 420 | 12.398 | 690.5 | 50 | 1500 | 0 | 0 | 0.07656 | 0
Load Test:
Load | Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
[p.u] | [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
0.25 | 400 | 11.59 | 4342.3 | 50 | 1492.8 | 23.9902 | 3750 | 0.54077 | 86.3598
0.5 | 400 | 16.01 | 8265 | 50 | 1486.2 | 48.1934 | 7500 | 0.74513 | 90.7441
0.75 | 400 | 21.19 | 12300 | 50 | 1479 | 72.642 | 11250 | 0.83783 | 91.4634
1 | 400 | 27.04 | 16468 | 50 | 1471 | 97.3827 | 15000 | 0.87905 | 91.0857
1.25 | 400 | 33.46 | 20790 | 50 | 1462.2 | 122.461 | 18750 | 0.89683 | 90.1876
1.5 | 400 | 40.35 | 25285 | 50 | 1452.7 | 147.9142 | 22500 | 0.90448 | 88.9856
Full Load At 380V & 420V
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
380V | 380 | 27.89 | 16430 | 50 | 1467.5 | 97.615 | 15000 | 0.89504 | 91.2964
420V | 420 | 26.57 | 16390 | 50 | 1474.5 | 97.1516 | 15000 | 0.84796 | 91.5192
Locked Rotor Test:
Un (V) |  | Ik (A) |  | Pk(W) |  | Tk (Nm) |  | cosφ
400/690 |  | 238.1 |  | 83616 |  | 250.9 |  | 0.5068
Temperature Rise:
Amb.Temperature: |  | 26.6 | [℃] |  |  |  | Winding temperature rise: | 73 | [K]
Cold Resistance: |  | 0.3968 | [Ω] |  |  |  | Frame: | 42 | [℃]
Hot Resistance: |  | 0.5084 | [Ω] |  |  |  | Bearing: | 55 | [℃]
Torque And Current:
|  | Locked Rotor Tor./Rated Tor.: | 2.53 |  |  |  |  | Breakdown Torque/Rated Torque: | 3.16
|  | Locked Rotor Cur./Rated Cur.: | 8.81 |  |  |  |  | Pullup Torque/Rated Torque: | 1.77
Check: | Zhang Kai |  | Operator: | Li Jian |  |  | Test Date: | 2012-06-07