## Sheet1
Type Test Report
Motor tested in accordance with IEC60034-2-1 & AS/NZS1359.102.3.Efficiency as per IEC60034-2-1
(PLL determined from residual loss)
SHANGHAI TOP MOTOR CO., LTD
No.303 Kangliu Road |  |  |  | Ph: 86 15000088129 |  |  | Type: | TCI 160M-4
Kang Qiao Industrial Area |  |  |  | zk@techtop.net.cn |  |  | TR Number: | 2012060602
Pudong, Shanghai, China |  |  |  | www.techtop.com |  |  | Test Lab: | Techtop factory
Nameplate:
Type: | TCI 160M-4 |  | Duty: | S1 | IP: | 55
Serial No: | 2012030704 |  | Ins.Cl: | F | KG: | 125
Voltage | Hz | kW | A | cos fi | r/min | Eff.[%]
400/690 | 50 | 11 | 20.4/11.8 | 0.86 | 1470 | 90.7
Brg.DE: | 6309C3 |  | Brg.NDE: | 6309C3
No Load Test:
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
No load | 370 | 6.94 | 330.5 | 50 | 1500 | 0 | 0 | 0.07431 | 0
No load | 400 | 8.6467 | 431.2 | 50 | 1500 | 0 | 0 | 0.071979 | 0
No load | 420 | 10.317 | 550.5 | 50 | 1500 | 0 | 0 | 0.073349 | 0
Load Test:
Load | Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
[p.u] | [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
0.25 | 400 | 9.552 | 3220.7 | 50 | 1493.5 | 17.5845 | 2750 | 0.48667 | 85.3852
0.5 | 400 | 12.44 | 6074.6 | 50 | 1487.3 | 35.3157 | 5500 | 0.70482 | 90.5409
0.75 | 400 | 16 | 8996.5 | 50 | 1480.6 | 53.2132 | 8250 | 0.81158 | 91.7023
1 | 400 | 20.13 | 12001 | 50 | 1473.2 | 71.3074 | 11000 | 0.8605 | 91.659
1.25 | 400 | 24.73 | 15101 | 50 | 1465.2 | 89.6209 | 13750 | 0.88138 | 91.0536
1.5 | 400 | 29.68 | 18307 | 50 | 1456.6 | 108.18 | 16500 | 0.89029 | 90.1295
Full Load At 380V & 420V
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
380V | 380 | 21.17 | 12260 | 50 | 1467.4 | 71.5892 | 11000 | 0.87988 | 89.7227
420V | 420 | 20.06 | 12110 | 50 | 1474.8 | 71.23 | 11000 | 0.82986 | 90.834
Locked Rotor Test:
Un (V) |  | Ik (A) |  | Pk(W) |  | Tk (Nm) |  | cosφ
400/690 |  | 168.7 |  | 59779 |  | 206 |  | 0.5114
Temperature Rise:
Amb.Temperature: |  | 27.7 | [℃] |  |  |  | Winding temperature rise: | 60.8 | [K]
Cold Resistance: |  | 0.5571 | [Ω] |  |  |  | Frame: | 45 | [℃]
Hot Resistance: |  | 0.6924 | [Ω] |  |  |  | Bearing: | 57 | [℃]
Torque And Current:
|  | Locked Rotor Tor./Rated Tor.: | 2.87 |  |  |  |  | Breakdown Torque/Rated Torque: | 3.29
|  | Locked Rotor Cur./Rated Cur.: | 8.38 |  |  |  |  | Pullup Torque/Rated Torque: | 2.03
Check: | Zhang Kai |  | Operator: | Li Jian |  |  | Test Date: | 2012-06-06