## Sheet1
Type Test Report
Motor tested in accordance with IEC60034-2-1 & AS/NZS1359.102.3.Efficiency as per IEC60034-2-1
(PLL determined from residual loss)
SHANGHAI TOP MOTOR CO., LTD
No.303 Kangliu Road |  |  |  | Ph: 86 15000088129 |  |  | Type: | TCI 250M-2
Kang Qiao Industrial Area |  |  |  | zk@techtop.net.cn |  |  | TR Number: | 2012061701
Pudong, Shanghai, China |  |  |  | www.techtop.com |  |  | Test Lab: | Techtop factory
Nameplate:
Type: | TCI 250M-2 |  | Duty: | S1 | IP: | 55
Serial No: | 2012030716 |  | Ins.Cl: | F | KG: | 420
Voltage | Hz | kW | A | cos fi | r/min | Eff.[%]
400/690 | 50 | 55 | 93.3/54.1 | 0.91 | 2970 | 93.5
Brg.DE: | 6314C3 |  | Brg.NDE: | 6314C3
No Load Test:
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
No load | 380 | 20.112 | 1484.5 | 50 | 3000 | 0 | 0 | 0.11215 | 0
No load | 400 | 21.98 | 1598.5 | 50 | 3000 | 0 | 0 | 0.10497 | 0
No load | 420 | 24.367 | 1710 | 50 | 3000 | 0 | 0 | 0.096468 | 0
Load Test:
Load | Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
[p.u] | [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
0.25 | 400 | 31.85 | 15448 | 50 | 2993.4 | 43.8673 | 13750 | 0.70007 | 89.0083
0.5 | 400 | 49.94 | 29495 | 50 | 2986.6 | 87.9344 | 27500 | 0.85247 | 93.2361
0.75 | 400 | 70.24 | 43744 | 50 | 2979.2 | 132.2293 | 41250 | 0.8989 | 94.2986
1 | 400 | 92.2 | 58221 | 50 | 2971.5 | 176.7626 | 55000 | 0.91144 | 94.4676
1.25 | 400 | 115.2 | 72941 | 50 | 2963.2 | 221.5721 | 68750 | 0.9139 | 94.2543
1.5 | 400 | 138.7 | 87912 | 50 | 2954.5 | 266.6695 | 82500 | 0.91485 | 93.8438
Full Load At 380V & 420V
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
380V | 380 | 96.88 | 58870 | 50 | 2966 | 177.0904 | 55000 | 0.92324 | 93.4262
420V | 420 | 90.02 | 58850 | 50 | 2972 | 176.7328 | 55000 | 0.89866 | 93.4579
Locked Rotor Test:
Un (V) |  | Ik (A) |  | Pk(W) |  | Tk (Nm) |  | cosφ
400/690 |  | 822.8 |  | 229291 |  | 535 |  | 0.4022
Temperature Rise:
Amb.Temperature: |  | 29.2 | [℃] |  |  |  | Winding temperature rise: | 58.8 | [K]
Cold Resistance: |  | 0.0564 | [Ω] |  |  |  | Frame: | 53 | [℃]
Hot Resistance: |  | 0.06945 | [Ω] |  |  |  | Bearing: | 65 | [℃]
Torque And Current:
|  | Locked Rotor Tor./Rated Tor.: | 3.02 |  |  |  |  | Breakdown Torque/Rated Torque: | 2.99
|  | Locked Rotor Cur./Rated Cur.: | 8.92 |  |  |  |  | Pullup Torque/Rated Torque: | 1.42
Check: | Zhang Kai |  | Operator: | Li Jian |  |  | Test Date: | 2012-06-17