## Sheet1
Type Test Report
Motor tested in accordance with IEC60034-2-1 & AS/NZS1359.102.3.Efficiency as per IEC60034-2-1
(PLL determined from residual loss)
SHANGHAI TOP MOTOR CO., LTD
No.303 Kangliu Road |  |  |  | Ph: 86 15000088129 |  |  | Type: | TCI 160L-6
Kang Qiao Industrial Area |  |  |  | zk@techtop.net.cn |  |  | TR Number: | 2012060801
Pudong, Shanghai, China |  |  |  | www.techtop.com |  |  | Test Lab: | Techtop factory
Nameplate:
Type: | TCI 160L-6 |  | Duty: | S1 | IP: | 55
Serial No: | 2012030707 |  | Ins.Cl: | F | KG: | 135
Voltage | Hz | kW | A | cos fi | r/min | Eff.[%]
400/690 | 50 | 11 | 23.8/13.8 | 0.75 | 975 | 89
Brg.DE: | 6309C3 |  | Brg.NDE: | 6309C3
No Load Test:
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
No load | 380 | 11.62 | 434.5 | 50 | 1000 | 0 | 0 | 0.056812 | 0
No load | 400 | 13.248 | 529.5 | 50 | 1000 | 0 | 0 | 0.057689 | 0
No load | 420 | 15.508 | 665 | 50 | 1000 | 0 | 0 | 0.058946 | 0
Load Test:
Load | Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
[p.u] | [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
0.25 | 400 | 13.93 | 3317.7 | 50 | 994.79 | 26.4 | 2750 | 0.34377 | 82.8887
0.5 | 400 | 16.25 | 6206.4 | 50 | 989.57 | 53.0786 | 5500 | 0.55127 | 88.6182
0.75 | 400 | 19.55 | 9195.4 | 50 | 983.76 | 80.0881 | 8250 | 0.6789 | 89.7188
1 | 400 | 23.66 | 12302 | 50 | 977.35 | 107.4845 | 11000 | 0.75048 | 89.4164
1.25 | 400 | 28.42 | 15545 | 50 | 970.36 | 135.3235 | 13750 | 0.78949 | 88.4529
1.5 | 400 | 33.65 | 18938 | 50 | 962.77 | 163.6684 | 16500 | 0.81232 | 87.1264
Full Load At 380V & 420V
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
380V | 380 | 23.62 | 12430 | 50 | 976 | 107.6332 | 11000 | 0.79955 | 88.4956
420V | 420 | 23.05 | 12410 | 50 | 981 | 107.0846 | 11000 | 0.7401 | 88.6382
Locked Rotor Test:
Un (V) |  | Ik (A) |  | Pk(W) |  | Tk (Nm) |  | cosφ
400/690 |  | 193.5 |  | 69319 |  | 334 |  | 0.5169
Temperature Rise:
Amb.Temperature: |  | 30.8 | [℃] |  |  |  | Winding temperature rise: | 89.2 | [K]
Cold Resistance: |  | 0.5083 | [Ω] |  |  |  | Frame: | 48 | [℃]
Hot Resistance: |  | 0.6552 | [Ω] |  |  |  | Bearing: | 62 | [℃]
Torque And Current:
|  | Locked Rotor Tor./Rated Tor.: | 3.09 |  |  |  |  | Breakdown Torque/Rated Torque: | 1.52
|  | Locked Rotor Cur./Rated Cur.: | 8.18 |  |  |  |  | Pullup Torque/Rated Torque: | 1.4
Check: | Zhang Kai |  | Operator: | Li Jian |  |  | Test Date: | 2012-06-08