## Sheet1
Type Test Report
Motor tested in accordance with IEC60034-2-1 & AS/NZS1359.102.3.Efficiency as per IEC60034-2-1
(PLL determined from residual loss)
SHANGHAI TOP MOTOR CO., LTD
No.303 Kangliu Road |  |  |  | Ph: 86 15000088129 |  |  | Type: | TCI 160M1-2
Kang Qiao Industrial Area |  |  |  | zk@techtop.net.cn |  |  | TR Number: | 2012060501
Pudong, Shanghai, China |  |  |  | www.techtop.com |  |  | Test Lab: | Techtop factory
Nameplate:
Type: | TCI 160M1-2 |  | Duty: | S1 | IP: | 55
Serial No: | 2012030701 |  | Ins.Cl: | F | KG: | 113
Voltage | Hz | kW | A | cos fi | r/min | Eff.[%]
400/690 | 50 | 11 | 19.5/11.3 | 0.91 | 2950 | 89.6
Brg.DE: | 6309C3 |  | Brg.NDE: | 6309C3
No Load Test:
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
No load | 380 | 4.6093 | 431.6 | 50 | 3000 | 0 | 0 | 0.14227 | 0
No load | 400 | 5.1833 | 473.8 | 50 | 3000 | 0 | 0 | 0.13194 | 0
No load | 420 | 5.9833 | 525.8 | 50 | 3000 | 0 | 0 | 0.1208 | 0
Load Test:
Load | Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
[p.u] | [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
0.25 | 400 | 7.053 | 3269.8 | 50 | 2988.6 | 8.7876 | 2750 | 0.66915 | 84.103
0.5 | 400 | 10.64 | 6157.7 | 50 | 2977.8 | 17.6389 | 5500 | 0.83533 | 89.3191
0.75 | 400 | 14.76 | 9141.9 | 50 | 2965.6 | 26.5671 | 8250 | 0.89398 | 90.2438
1 | 400 | 19.35 | 12239 | 50 | 2952.2 | 35.5836 | 11000 | 0.91294 | 89.8766
1.25 | 400 | 24.34 | 15465 | 50 | 2937.3 | 44.7052 | 13750 | 0.91708 | 88.9104
1.5 | 400 | 29.67 | 18835 | 50 | 2921.2 | 53.9419 | 16500 | 0.91628 | 87.6029
Full Load At 380V & 420V
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
380V | 380 | 20.15 | 12180 | 50 | 2943.8 | 35.6852 | 11000 | 0.91839 | 90.312
420V | 420 | 18.75 | 12150 | 50 | 2956.6 | 35.5307 | 11000 | 0.89077 | 90.535
Locked Rotor Test:
Un (V) |  | Ik (A) |  | Pk(W) |  | Tk (Nm) |  | cosφ
400/690 |  | 166 |  | 56560 |  | 91.55 |  | 0.4918
Temperature Rise:
Amb.Temperature: |  | 28.3 | [℃] |  |  |  | Winding temperature rise: | 61.1 | [K]
Cold Resistance: |  | 0.5553 | [Ω] |  |  |  | Frame: | 50 | [℃]
Hot Resistance: |  | 0.6866 | [Ω] |  |  |  | Bearing: | 60 | [℃]
Torque And Current:
|  | Locked Rotor Tor./Rated Tor.: | 2.6 |  |  |  |  | Breakdown Torque/Rated Torque: | 3.02
|  | Locked Rotor Cur./Rated Cur.: | 8.58 |  |  |  |  | Pullup Torque/Rated Torque: | 0.93
Check: | Zhang Kai |  | Operator: | Li Jian |  |  | Test Date: | 2012-06-05