## Sheet1
Type Test Report
Motor tested in accordance with IEC60034-2-1 & AS/NZS1359.102.3.Efficiency as per IEC60034-2-1
(PLL determined from residual loss)
SHANGHAI TOP MOTOR CO., LTD
No.303 Kangliu Road |  |  |  | Ph: 86 15000088129 |  |  | Type: | TCI 160M2-2
Kang Qiao Industrial Area |  |  |  | zk@techtop.net.cn |  |  | TR Number: | 2012060502
Pudong, Shanghai, China |  |  |  | www.techtop.com |  |  | Test Lab: | Techtop factory
Nameplate:
Type: | TCI 160M2-2 |  | Duty: | S1 | IP: | 55
Serial No: | 2012030702 |  | Ins.Cl: | F | KG: | 132
Voltage | Hz | kW | A | cos fi | r/min | Eff.[%]
400/690 | 50 | 15 | 26.2/15.2 | 0.91 | 2950 | 90.8
Brg.DE: | 6309C3 |  | Brg.NDE: | 6309C3
No Load Test:
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
No load | 380 | 6.298 | 437.8 | 50 | 3000 | 0 | 0 | 0.10562 | 0
No load | 400 | 6.9417 | 590 | 50 | 3000 | 0 | 0 | 0.12268 | 0
No load | 420 | 7.76 | 523 | 50 | 3000 | 0 | 0 | 0.092647 | 0
Load Test:
Load | Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
[p.u] | [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
0.25 | 400 | 9.457 | 4324.4 | 50 | 2990.1 | 11.977 | 3750 | 0.66001 | 86.7172
0.5 | 400 | 14.21 | 8221.2 | 50 | 2980.1 | 24.0344 | 7500 | 0.83507 | 91.2276
0.75 | 400 | 19.68 | 12219 | 50 | 2969.2 | 36.184 | 11250 | 0.89617 | 92.0697
1 | 400 | 25.75 | 16335 | 50 | 2957.3 | 48.4395 | 15000 | 0.91563 | 91.8274
1.25 | 400 | 32.27 | 20583 | 50 | 2944.4 | 60.8146 | 18750 | 0.92064 | 91.0946
1.5 | 400 | 39.12 | 24972 | 50 | 2930.4 | 73.3262 | 22500 | 0.92137 | 90.1009
Full Load At 380V & 420V
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
380V | 380 | 27.12 | 16550 | 50 | 2944.6 | 48.6484 | 15000 | 0.92718 | 90.6344
420V | 420 | 24.84 | 16410 | 50 | 2957.5 | 48.4362 | 15000 | 0.90813 | 91.4077
Locked Rotor Test:
Un (V) |  | Ik (A) |  | Pk(W) |  | Tk (Nm) |  | cosφ
400/690 |  | 232 |  | 82613 |  | 125.6 |  | 0.514
Temperature Rise:
Amb.Temperature: |  | 28.6 | [℃] |  |  |  | Winding temperature rise: | 64.1 | [K]
Cold Resistance: |  | 0.3741 | [Ω] |  |  |  | Frame: | 48 | [℃]
Hot Resistance: |  | 0.4672 | [Ω] |  |  |  | Bearing: | 58 | [℃]
Torque And Current:
|  | Locked Rotor Tor./Rated Tor.: | 2.57 |  |  |  |  | Breakdown Torque/Rated Torque: | 3.16
|  | Locked Rotor Cur./Rated Cur.: | 9.01 |  |  |  |  | Pullup Torque/Rated Torque: | 1.32
Check: | Zhang Kai |  | Operator: | Li Jian |  |  | Test Date: | 2012-06-05