## Sheet1
Type Test Report
Motor tested in accordance with IEC60034-2-1 & AS/NZS1359.102.3.Efficiency as per IEC60034-2-1
(PLL determined from residual loss)
SHANGHAI TOP MOTOR CO., LTD
No.303 Kangliu Road |  |  |  | Ph: 86 15000088129 |  |  | Type: | TCI 180M-4
Kang Qiao Industrial Area |  |  |  | zk@techtop.net.cn |  |  | TR Number: | 2012120201
Pudong, Shanghai, China |  |  |  | www.techtop.com |  |  | Test Lab: | Techtop factory
Nameplate:
Type: | TCI 180M-4 |  | Duty: | S1 | IP: | 55
Serial No: | 2012091101 |  | Ins.Cl: | F | KG: | 158
Voltage | Hz | kW | A | cos fi | r/min | Eff.[%]
400/690 | 50 | 18.5 | 33.2/19.2 | 0.88 | 1470 | 91.4
Brg.DE: | 6311C3 |  | Brg.NDE: | 6311C3
No Load Test:
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
No load | 370 | 10.352 | 535.5 | 50 | 1500 | 0 | 0 | 0.080718 | 0
No load | 400 | 12.235 | 646 | 50 | 1500 | 0 | 0 | 0.076209 | 0
No load | 420 | 14.162 | 768 | 50 | 1500 | 0 | 0 | 0.074546 | 0
Load Test:
Load | Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
[p.u] | [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
0.25 | 400 | 14.38 | 5336.5 | 50 | 1493.1 | 29.5819 | 4625 | 0.53564 | 86.6673
0.5 | 400 | 19.51 | 10144 | 50 | 1486.4 | 59.4305 | 9250 | 0.75047 | 91.1869
0.75 | 400 | 25.78 | 15078 | 50 | 1479.1 | 89.5857 | 13875 | 0.84419 | 92.0215
1 | 400 | 33.01 | 20163 | 50 | 1471 | 120.1054 | 18500 | 0.88164 | 91.7522
1.25 | 400 | 41 | 25421 | 50 | 1462.1 | 15.1209 | 2315 | 0.89493 | 9.1066
1.5 | 400 | 49.55 | 30870 | 50 | 1452.6 | 182.4401 | 27750 | 0.89923 | 89.8931
Full Load At 380V & 420V
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
380V | 380 | 35.71 | 20180 | 50 | 1466 | 120.515 | 18500 | 0.85859 | 91.6749
420V | 420 | 36.29 | 20160 | 50 | 1473 | 119.9423 | 18500 | 0.76365 | 91.7659
Locked Rotor Test:
Un (V) |  | Ik (A) |  | Pk(W) |  | Tk (Nm) |  | cosφ
400/690 |  | 259.3 |  | 91782 |  | 303.6 |  | 0.5108
Temperature Rise:
Amb.Temperature: |  | 13 | [℃] |  |  |  | Winding temperature rise: | 44.6 | [K]
Cold Resistance: |  | 0.2666 | [Ω] |  |  |  | Frame: | 31 | [℃]
Hot Resistance: |  | 0.31613 | [Ω] |  |  |  | Bearing: | 43 | [℃]
Torque And Current:
|  | Locked Rotor Tor./Rated Tor.: | 2.54 |  |  |  |  | Breakdown Torque/Rated Torque: | 3.11
|  | Locked Rotor Cur./Rated Cur.: | 7.86 |  |  |  |  | Pullup Torque/Rated Torque: | 1.94
Check: | Zhang Kai |  | Operator: | Li Jian |  |  | Test Date: | 2012-12-02