## Sheet1
Type Test Report
Motor tested in accordance with IEC60034-2-1 & AS/NZS1359.102.3.Efficiency as per IEC60034-2-1
(PLL determined from residual loss)
SHANGHAI TOP MOTOR CO., LTD
No.303 Kangliu Road |  |  |  | Ph: 86 15000088129 |  |  | Type: | TCI 200L1-2
Kang Qiao Industrial Area |  |  |  | zk@techtop.net.cn |  |  | TR Number: | 2012061101
Pudong, Shanghai, China |  |  |  | www.techtop.com |  |  | Test Lab: | Techtop factory
Nameplate:
Type: | TCI 200L1-2 |  | Duty: | S1 | IP: | 55
Serial No: | 2012030710 |  | Ins.Cl: | F | KG: | 233
Voltage | Hz | kW | A | cos fi | r/min | Eff.[%]
400/690 | 50 | 30 | 52.9/30.7 | 0.89 | 2955 | 92
Brg.DE: | 6312C3 |  | Brg.NDE: | 6312C3
No Load Test:
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
No load | 380 | 12.002 | 916 | 50 | 3000 | 0 | 0 | 0.11596 | 0
No load | 400 | 13.453 | 990.5 | 50 | 3000 | 0 | 0 | 0.10627 | 0
No load | 420 | 15.437 | 1102.5 | 50 | 3000 | 0 | 0 | 0.098176 | 0
Load Test:
Load | Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
[p.u] | [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
0.25 | 400 | 18.52 | 8593.3 | 50 | 2989.2 | 23.9613 | 7500 | 0.66973 | 87.2773
0.5 | 400 | 28.57 | 16384 | 50 | 2978.8 | 48.0898 | 15000 | 0.82773 | 91.5527
0.75 | 400 | 39.87 | 24377 | 50 | 2966.9 | 72.4241 | 22500 | 0.8825 | 92.3001
1 | 400 | 52.39 | 32610 | 50 | 2956.6 | 96.9018 | 30000 | 0.89842 | 91.9963
1.25 | 400 | 66.08 | 41125 | 50 | 2938.7 | 121.8651 | 37500 | 0.89829 | 91.1854
1.5 | 400 | 80.89 | 49966 | 50 | 2922.3 | 147.0588 | 45000 | 0.89158 | 90.0612
Full Load At 380V & 420V
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
380V | 380 | 54.94 | 32790 | 50 | 2937.3 | 97.5386 | 30000 | 0.90679 | 91.4913
420V | 420 | 50.32 | 32490 | 50 | 2952.9 | 97.0233 | 30000 | 0.88756 | 92.3361
Locked Rotor Test:
Un (V) |  | Ik (A) |  | Pk(W) |  | Tk (Nm) |  | cosφ
400/690 |  | 368.5 |  | 105803 |  | 199.5 |  | 0.4144
Temperature Rise:
Amb.Temperature: |  | 28.5 | [℃] |  |  |  | Winding temperature rise: | 76.5 | [K]
Cold Resistance: |  | 0.1613 | [Ω] |  |  |  | Frame: | 55 | [℃]
Hot Resistance: |  | 0.2084 | [Ω] |  |  |  | Bearing: | 65 | [℃]
Torque And Current:
|  | Locked Rotor Tor./Rated Tor.: | 2.05 |  |  |  |  | Breakdown Torque/Rated Torque: | 2.54
|  | Locked Rotor Cur./Rated Cur.: | 7.03 |  |  |  |  | Pullup Torque/Rated Torque: | 1.04
Check: | Zhang Kai |  | Operator: | Li Jian |  |  | Test Date: | 2012-06-11