## Sheet1
Type Test Report
Motor tested in accordance with IEC60034-2-1 & AS/NZS1359.102.3.Efficiency as per IEC60034-2-1
(PLL determined from residual loss)
SHANGHAI TOP MOTOR CO., LTD
No.303 Kangliu Road |  |  |  | Ph: 86 15000088129 |  |  | Type: | TCI 200L-4
Kang Qiao Industrial Area |  |  |  | zk@techtop.net.cn |  |  | TR Number: | 2012061201
Pudong, Shanghai, China |  |  |  | www.techtop.com |  |  | Test Lab: | Techtop factory
Nameplate:
Type: | TCI 200L-4 |  | Duty: | S1 | IP: | 55
Serial No: | 2012030711 |  | Ins.Cl: | F | KG: | 242
Voltage | Hz | kW | A | cos fi | r/min | Eff.[%]
400/690 | 50 | 30 | 57.2/33.2 | 0.82 | 1480 | 92.3
Brg.DE: | 6312C3 |  | Brg.NDE: | 6312C3
No Load Test:
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
No load | 370 | 21.38 | 728 | 50 | 1500 | 0 | 0 | 0.053133 | 0
No load | 400 | 26.91 | 999 | 50 | 1500 | 0 | 0 | 0.053584 | 0
No load | 420 | 32.02 | 1290 | 50 | 1500 | 0 | 0 | 0.055381 | 0
Load Test:
Load | Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
[p.u] | [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
0.25 | 400 | 29.65 | 8590.9 | 50 | 1495.1 | 47.9065 | 7500 | 0.41821 | 87.3017
0.5 | 400 | 36.58 | 16345 | 50 | 1490.8 | 96.0893 | 15000 | 0.64494 | 91.7712
0.75 | 400 | 45.84 | 24277 | 50 | 1485.9 | 144.6093 | 22500 | 0.76442 | 92.6803
1 | 400 | 56.95 | 32422 | 50 | 1480.5 | 193.5157 | 30000 | 0.82172 | 92.5298
1.25 | 400 | 69.43 | 40806 | 50 | 1474.7 | 242.846 | 37500 | 0.84831 | 91.8983
1.5 | 400 | 82.8 | 49444 | 50 | 1468.3 | 292.6854 | 45000 | 0.86191 | 91.0121
Full Load At 380V & 420V
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
380V | 380 | 56.61 | 32420 | 50 | 1477 | 193.9743 | 30000 | 0.87011 | 92.5355
420V | 420 | 57.31 | 32520 | 50 | 1481 | 193.4504 | 30000 | 0.78003 | 92.2509
Locked Rotor Test:
Un (V) |  | Ik (A) |  | Pk(W) |  | Tk (Nm) |  | cosφ
400/690 |  | 463.4 |  | 166190 |  | 457.9 |  | 0.5176
Temperature Rise:
Amb.Temperature: |  | 28.7 | [℃] |  |  |  | Winding temperature rise: | 71.7 | [K]
Cold Resistance: |  | 0.1746 | [Ω] |  |  |  | Frame: | 52 | [℃]
Hot Resistance: |  | 0.2345 | [Ω] |  |  |  | Bearing: | 66 | [℃]
Torque And Current:
|  | Locked Rotor Tor./Rated Tor.: | 2.37 |  |  |  |  | Breakdown Torque/Rated Torque: | 2.95
|  | Locked Rotor Cur./Rated Cur.: | 8.14 |  |  |  |  | Pullup Torque/Rated Torque: | 1.91
Check: | Zhang Kai |  | Operator: | Li Jian |  |  | Test Date: | 2012-06-12