## Sheet1
Type Test Report
Motor tested in accordance with IEC60034-2-1 & AS/NZS1359.102.3.Efficiency as per IEC60034-2-1
(PLL determined from residual loss)
SHANGHAI TOP MOTOR CO., LTD
No.303 Kangliu Road |  |  |  | Ph: 86 15000088129 |  |  | Type: | TCI 225M-4
Kang Qiao Industrial Area |  |  |  | zk@techtop.net.cn |  |  | TR Number: | 2012120401
Pudong, Shanghai, China |  |  |  | www.techtop.com |  |  | Test Lab: | Techtop factory
Nameplate:
Type: | TCI 225M-4 |  | Duty: | S1 | IP: | 55
Serial No: | 2012091105 |  | Ins.Cl: | F | KG: | 352
Voltage | Hz | kW | A | cos fi | r/min | Eff.[%]
400/690 | 50 | 45 | 85.1/49.3 | 0.82 | 1475 | 93.1
Brg.DE: | 6313C3 |  | Brg.NDE: | 6313C3
No Load Test:
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
No load | 350 | 24.707 | 1138 | 50 | 1500 | 0 | 0 | 0.075979 | 0
No load | 400 | 35.46 | 1692 | 50 | 1500 | 0 | 0 | 0.068872 | 0
No load | 450 | 56.8 | 3132 | 50 | 1500 | 0 | 0 | 0.070746 | 0
Load Test:
Load | Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
[p.u] | [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
0.25 | 400 | 40.58 | 13038 | 50 | 1495.5 | 71.8405 | 11250 | 0.46374 | 86.2862
0.5 | 400 | 52.11 | 24578 | 50 | 1490.8 | 144.134 | 22500 | 0.68078 | 91.5453
0.75 | 400 | 66.84 | 36326 | 50 | 1485.5 | 216.9724 | 33750 | 0.78444 | 92.9087
1 | 400 | 84.07 | 48313 | 50 | 1479.5 | 290.4698 | 45000 | 0.82947 | 93.1426
1.25 | 400 | 103.1 | 60570 | 50 | 1472.8 | 364.7389 | 56250 | 0.84797 | 92.8678
1.5 | 400 | 123.2 | 73127 | 50 | 1465.5 | 439.8669 | 67500 | 0.85673 | 92.3052
Full Load At 380V & 420V
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
380V | 380 | 82.48 | 48310 | 50 | 1478 | 290.7645 | 45000 | 0.88991 | 93.1484
420V | 420 | 78.58 | 48220 | 50 | 1482 | 289.9798 | 45000 | 0.84354 | 93.3223
Locked Rotor Test:
Un (V) |  | Ik (A) |  | Pk(W) |  | Tk (Nm) |  | cosφ
400/690 |  | 584.4 |  | 144826 |  | 604.7 |  | 0.3577
Temperature Rise:
Amb.Temperature: |  | 16 | [℃] |  |  |  | Winding temperature rise: | 55.9 | [K]
Cold Resistance: |  | 0.0445 | [Ω] |  |  |  | Frame: | 29.5 | [℃]
Hot Resistance: |  | 0.05426 | [Ω] |  |  |  | Bearing: | 33 | [℃]
Torque And Current:
|  | Locked Rotor Tor./Rated Tor.: | 2.07 |  |  |  |  | Breakdown Torque/Rated Torque: | 3.33
|  | Locked Rotor Cur./Rated Cur.: | 6.95 |  |  |  |  | Pullup Torque/Rated Torque: | 1.87
Check: | Zhang Kai |  | Operator: | Li Jian |  |  | Test Date: | 2012-12-04