## Sheet1
Type Test Report
Motor tested in accordance with IEC60034-2-1 & AS/NZS1359.102.3.Efficiency as per IEC60034-2-1
(PLL determined from residual loss)
SHANGHAI TOP MOTOR CO., LTD
No.303 Kangliu Road |  |  |  | Ph: 86 15000088129 |  |  | Type: | TCI 225M-2
Kang Qiao Industrial Area |  |  |  | zk@techtop.net.cn |  |  | TR Number: | 2012061401
Pudong, Shanghai, China |  |  |  | www.techtop.com |  |  | Test Lab: | Techtop factory
Nameplate:
Type: | TCI 225M-2 |  | Duty: | S1 | IP: | 55
Serial No: | 2012030714 |  | Ins.Cl: | F | KG: | 322
Voltage | Hz | kW | A | cos fi | r/min | Eff.[%]
400/690 | 50 | 45 | 77.6/45.0 | 0.9 | 2955 | 93
Brg.DE: | 6313C3 |  | Brg.NDE: | 6313C3
No Load Test:
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
No load | 380 | 15.697 | 1085.5 | 50 | 3000 | 0 | 0 | 0.10507 | 0
No load | 400 | 19.018 | 1260 | 50 | 3000 | 0 | 0 | 0.095628 | 0
No load | 420 | 22.16 | 1459 | 50 | 3000 | 0 | 0 | 0.090506 | 0
Load Test:
Load | Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
[p.u] | [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
0.25 | 400 | 26.55 | 12642 | 50 | 2990.9 | 35.9215 | 11250 | 0.68728 | 88.9891
0.5 | 400 | 41.58 | 24255 | 50 | 2981.6 | 72.067 | 22500 | 0.84197 | 92.7644
0.75 | 400 | 58.44 | 36118 | 50 | 2971.4 | 108.4716 | 33750 | 0.89206 | 93.4437
1 | 400 | 76.9 | 48266 | 50 | 2960.3 | 145.1711 | 45000 | 0.90593 | 93.2333
1.25 | 400 | 96.75 | 60736 | 50 | 2948.2 | 182.2086 | 56250 | 0.9061 | 92.6139
1.5 | 400 | 117.8 | 73563 | 50 | 2935.2 | 219.6188 | 67500 | 0.90135 | 91.7581
Full Load At 380V & 420V
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
380V | 380 | 80.73 | 49310 | 50 | 2953 | 145.53 | 45000 | 0.92802 | 91.2594
420V | 420 | 75.76 | 48120 | 50 | 2962 | 145.0878 | 45000 | 0.87312 | 93.5162
Locked Rotor Test:
Un (V) |  | Ik (A) |  | Pk(W) |  | Tk (Nm) |  | cosφ
400/690 |  | 572.3 |  | 164874 |  | 399.3 |  | 0.4158
Temperature Rise:
Amb.Temperature: |  | 31 | [℃] |  |  |  | Winding temperature rise: | 86.6 | [K]
Cold Resistance: |  | 0.07508 | [Ω] |  |  |  | Frame: | 58 | [℃]
Hot Resistance: |  | 0.09625 | [Ω] |  |  |  | Bearing: | 67 | [℃]
Torque And Current:
|  | Locked Rotor Tor./Rated Tor.: | 2.73 |  |  |  |  | Breakdown Torque/Rated Torque: | 2.51
|  | Locked Rotor Cur./Rated Cur.: | 7.44 |  |  |  |  | Pullup Torque/Rated Torque: | 1.13
Check: | Zhang Kai |  | Operator: | Li Jian |  |  | Test Date: | 2012-06-14