## Sheet1
Type Test Report
Motor tested in accordance with IEC60034-2-1 & AS/NZS1359.102.3.Efficiency as per IEC60034-2-1
(PLL determined from residual loss)
SHANGHAI TOP MOTOR CO., LTD
No.303 Kangliu Road |  |  |  | Ph: 86 15000088129 |  |  | Type: | TCI 225S-4
Kang Qiao Industrial Area |  |  |  | zk@techtop.net.cn |  |  | TR Number: | 2012120501
Pudong, Shanghai, China |  |  |  | www.techtop.com |  |  | Test Lab: | Techtop factory
Nameplate:
Type: | TCI 225S-4 |  | Duty: | S1 | IP: | 55
Serial No: | 2012091104 |  | Ins.Cl: | F | KG: | 315
Voltage | Hz | kW | A | cos fi | r/min | Eff.[%]
400/690 | 50 | 37 | 65.4/37.9 | 0.88 | 1475 | 92.8
Brg.DE: | 6313C3 |  | Brg.NDE: | 6313C3
No Load Test:
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
No load | 370 | 16.347 | 710.3 | 50 | 1500 | 0 | 0 | 0.067802 | 0
No load | 400 | 19.11 | 846.25 | 50 | 1500 | 0 | 0 | 0.063917 | 0
No load | 420 | 21.976 | 986.3 | 50 | 1500 | 0 | 0 | 0.061695 | 0
Load Test:
Load | Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
[p.u] | [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
1.25 | 415 | 81.21 | 40480 | 50 | 1475 | 299.4492 | 46250 | 0.69346 | 114.254
1 | 415 | 66.05 | 40580 | 50 | 1480 | 238.75 | 37000 | 0.85473 | 91.1779
0.75 | 415 | 52.14 | 30590 | 50 | 1486 | 178.3395 | 27750 | 0.81621 | 90.7159
0.5 | 415 | 40.05 | 20690 | 50 | 1491 | 118.4943 | 18500 | 0.7187 | 89.4152
0.25 | 415 | 30.34 | 11170 | 50 | 1496 | 59.0491 | 9250 | 0.51219 | 82.8111
Full Load At 380V & 420V
| Voltage | Current | Input | Freq. | Speed | Torque | Output | Power | Eff.
| [V] | [A] | [W] | [Hz] | [min-1] | [Nm] | [W] | Factor | [%]
380V | 380 | 68.22 | 40240 | 50 | 1475 | 239.5593 | 37000 | 0.89619 | 91.9483
420V | 420 | 62.72 | 39900 | 50 | 1481.1 | 238.5727 | 37000 | 0.87449 | 92.7318
Locked Rotor Test:
Un (V) |  | Ik (A) |  | Pk(W) |  | Tk (Nm) |  | cosφ
400/690 |  | 481.6 |  | 148480 |  | 531.3 |  | 0.445
Temperature Rise:
Amb.Temperature: |  | 9.1 | [℃] |  |  |  | Winding temperature rise: | 73.8 | [K]
Cold Resistance: |  | 0.10749 | [Ω] |  |  |  | Frame: | 39 | [℃]
Hot Resistance: |  | 0.14148 | [Ω] |  |  |  | Bearing: | 50 | [℃]
Torque And Current:
|  | Locked Rotor Tor./Rated Tor.: | 2.22 |  |  |  |  | Breakdown Torque/Rated Torque: | 2.43
|  | Locked Rotor Cur./Rated Cur.: | 7.43 |  |  |  |  | Pullup Torque/Rated Torque: | 1.47
Check: | Zhang Kai |  | Operator: | Li Jian |  |  | Test Date: | 2012-12-05